jk"Vªh; jkt/kkuh {ks= fnYyh ljdkj

GOVT. OF NATIONAL CAPITAL TERRITORY OF DELHI



yksd fuekZ.k foHkkx

PUBLIC WORKS DEPARTMENT

dk;kZy; v/kh{k.k vfHk;Urk

yks0fu0fo0 oS/kqr vuq0 ifjeaMy ,e-&45

(fnYyh ljdkj) rsjgoha ry]

yks0fu0fo0 eq[;ky; Hkou

vkbZ0 ih0 ,LVsV] ubZ fnYyh&110 002

nwjHkk”k % 011-23490441@23490443 QSDl % 23490442

**OFFICE OF THE SUPERINTENDING ENGINEER**

**PUBLIC WORKS DEPARTMENT**

**ELECTRICAL MAINTENANCE CIRCLE M-45,**

**GNCTD, 13TH FLOOR, MSO BUILDING,**

**I.P. ESTATE, NEW DELHI- 110 002.**

**Phone: 011-23490441/23490443 Fax : 23490442**

**E-mail:** **seepwddelhim45@gmail.com**

Lak[;k: 23(1)/SL/PWDEMCM-45/13-14/ fnukad: @ @2014

**INSPECTION NOTE**

Superintending Engineer (E), M-45 inspected the Electrical & Mechnical works at NHMC and Hospital Block, at Defence Colony, New Delhi alongwith Shri K.L. Balodhi, Executive Engineer(E) M-453 and Shri Pankaj Krishak, Assistant Engineer (E) M-4533 on 03.04.2014.

Following observation have been made:-

1. Out of 3 lifts, two lifts are working and one lifts is not working and hence necessary action is to be taken in this regard.
2. Many conduits are found unused and abandoned on the walls and these are to be removed.
3. Some light fittings are not working and these are to be made functional.
4. Compound lighting are to be made functional.
5. At many places, covers for junction/inspection boxes of conduits are not found at the ceiling and these are to be covered properly.
6. Servicing of Air Conditioners, Desert coolers, RO System are to be done.
7. Required insulation of exhaust pipe of diesel engine in the fire pump room is not done.
8. Exit Signages are installed but electrical socket are not provided to energise these signages.
9. There was leakage of water in the valve connected to wet riser at IInd floor of the Hospital Block and necessary action is to be taken to stop the leakage.

 **Superintending Engineer (E)**

PWD, EMC M-45, (GNCTD)

MSO Bldg., New Delhi

Copy to:-

1. Chief Engineer, PWD Maint. Zone M-4, 9th floor, MSO Bldg., New Delhi for information please.
2. Executive Executive(E), PWD EMD M-453, 11th Floor, MSO bldg., New Delhi for information & necessary action.

**Superintending Engineer (E)**